..\WorkInstructions\74.pdf

For Mechanical Check/Visual Inspection and Electrical Tests Use C.L. of W.I. 74

- RELAY DETAILS:

| Type : | P643 | Designation | 87T-2 |
| --- | --- | --- | --- |
| Model No : |  | PANEL REF |  |
| Serial Number |  | Nominal Current : In | 1.0 A |
| Make | ALSTOM | Aux. Volts of Relay : Vx | 110-250 V DC |
| FREQUENCY |  | 60Hz |  |

- TRANSFORMER DETAILS:

| Rated Power (MVA) | 100MVA |
| --- | --- |
| Primary Voltage (KV) | 132 KV |
| Secondary Voltage (KV) | 33 KV |
| Transformer Primary CT Ratio (A) | 600 / 1 A |
| Transformer Secondary CT Ratio (A) | 2400 / 1 A |
| Vector Group Reference | YNyn0+d1 |
| Zero Sequence filter | ON |
| NER CT Ratio | 1000/1A |

- VISUAL INSPECTION:

| Sl. No | Description | Checked |
| --- | --- | --- |
| 1 | Inspect For Physical Damage / Defects |  |
| 2 | Verify Connections As Per Approved Drawing |  |
| 3 | Check Tightness Of All Connections |  |
| 4 | Check relay software version |  |
| 5 | Relay Case Earthing Checked |  |

- GENERAL CHECK:

| CHECKING |  | RESULTS |
| --- | --- | --- |
| Dry cell Battery voltage (Remove battery isolation strip) |  |  |
| Auxiliary voltage on terminal J2 (+) and J1 (-) |  |  |
| Measured field supply voltage J7 – J9 and J8 – J10 |  |  |
| Watchdog contact when relay OFF | Terminals J11 and J12 CLOSED |  |
|  | Terminals J13 and J14 OPEN |  |
| Watchdog contact when relay ON | Terminals J11 and J12 OPEN |  |
|  | Terminals J13 and J14 CLOSED |  |
| Check if the frequency is set on required value |  |  |

- MEASUREMENT VALUE TEST:

CT Ratio:

Primary side – a:  600A					Secondary side – a: 1 A

Primary side – b: 2400 A				          Secondary side – b: 1 A

| Side | Inj. Current ( A ) | Calculated Current ( A ) | Relay Reading ( A ) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | R |  | Y |  | B |  |
|  |  |  | Prim | % Er | Prim. | % Er | Prim. | % Er |
| HV | 1.00 | 600 |  |  |  |  |  |  |
| LV | 1.00 | 2400 |  |  |  |  |  |  |

Deviation: +/- 1% Manual P64x/EN TD/A32 – Technical Data – Page No. 4

REF NEUTRAL CT:

| Phase( IN) | CT ratio | Inj. Current(A) | Calculated current(A) | Relay Reading |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | Pri | % Er |
| TN1 | 600/1A | 1A | 600 |  |  |
| TN2 | 2400/1A | 1A | 2400 |  |  |

Deviation: +/- 1% Manual P64x/EN TD/A32 – Technical Data – Page No. 4

VOLTAGE MEASUREMENT:

| Phase | Applied Voltage(V) | Calculated Voltage(KV) | Relay Reading(KV) | % Er |
| --- | --- | --- | --- | --- |
| VAN | 63.5 | 19.05 |  |  |
| VBN | 63.5 | 19.05 |  |  |
| VCN | 63.5 | 19.05 |  |  |
| VAB | 110 | 33.0 |  |  |
| VBC | 110 | 33.0 |  |  |
| VCA | 110 | 33.0 |  |  |

Deviation: +/- 1% Manual P64x/EN TD/A32 – Technical Data – Page No. 4

- DIFFERENTIAL ELEMENT:

Iref a (Prim) = Sref /√3* Vnom a       = (100MVA/1.732*132KV) =  437.4 A

Iref b (Prim) = Sref /√3* Vnom b       = (100MVA/1.732*33.0KV) = 1749.5 A

Kam,a = CT Ratio a / Iref a               = 1.372

Kam,b = CT Ratio b / Iref b               = 1.372

Where:

Iref a (Prim)………………............    HV full load current (Primary value)

Iref b (Prim)………………............    LV full load current (Primary value)

Sref ………………………………     Transformer capacity

Vnom a…………………………..     Transformer HV Side voltage

Vnom b…………………………..     Transformer LV Side voltage

CT Ratio a.………………………     Transformer HV Side phase CT ratio

CT Ratio b.………………………     Transformer LV Side phase CT ratio

Kam,a……………………………     Winding “a” amplitude matching factor

Kam,b……………………………     Winding “b” amplitude matching factor

TRIPPING CHARACTERISTIC

- LOW SET ELEMENT CURRENT SENSITIVITY TEST (Is1):

Objective: To test threshold Is1:

Pick up Condition: Is1/2<= ibias

Test method:

Inject balanced currents in all phases (one by one)

Gradually increase currents till relay operation. Note down the value.

Calculation: For example Is1 = 0.27

Side a Pick up = Is1 / Kam,a = 0.27/1.372 = 0.196

Side b Pick up = Is1 /Kam,b =   0.27/1.372 = 0.196

Pick up Current Ia           =   0.196

Pick up Current Ib           =   0.196

Because of zero sequence filter ON (for single phase)

HV side   0.196 x 1.5 =   0.295

LV side   0.196 x 1.5 =   0.295

HV SIDE

| Phase | Setting | Expected | Pickup (A) | Timing (ms) |
| --- | --- | --- | --- | --- |
| R – E | 0.27 | 0.295 |  |  |
| Y – E | 0.27 | 0.295 |  |  |
| B – E | 0.27 | 0.295 |  |  |
| RYB | 0.27 | 0.196 |  |  |

Deviation: +/-5% Manual P64x/EN TD/A32 – Technical data – Page no. 42

LV SIDE

| Phase | Setting | Expected | Pickup (A) | Timing (ms) |
| --- | --- | --- | --- | --- |
| R – E | 0.27 | 0.295 |  |  |
| Y – E | 0.27 | 0.295 |  |  |
| B – E | 0.27 | 0.295 |  |  |
| RYB | 0.27 | 0.196 |  |  |

Deviation: +/-5% Manual P64x/EN TD/A32 – Technical data – Page no. 42

- HIGH SET ELEMENT CURRENT SENSITIVITY TEST (Is-Hs1):

NOTE: INJECT ANY ONE SIDE WITH HARMONICS

HV SIDE

| Phase | Setting | Expected | Pickup (A) | Timing (ms) |
| --- | --- | --- | --- | --- |
| R – E | 5.5 pu | 6.01 A |  |  |
| Y – E | 5.5 pu | 6.01 A |  |  |
| B – E | 5.5 pu | 6.01 A |  |  |
| R-Y-B | 5.5 pu | 4.0 A |  |  |

Deviation: +/-5% Manual P64x/EN TD/A32 – Technical data – Page no. 42

LV SIDE

| Phase | Setting | Expected | Pickup (A) | Timing (ms) |
| --- | --- | --- | --- | --- |
| R – E | 5.5 pu | 6.01 A |  |  |
| Y – E | 5.5 pu | 6.01 A |  |  |
| B – E | 5.5 pu | 6.01 A |  |  |
| R-Y-B | 5.5 pu | 4.0 A |  |  |

Deviation: +/-5% Manual P64x/EN TD/A32 – Technical data – Page no. 42

- HIGH SET ELEMENT CURRENT SENSITIVITY TEST (Is-Hs2):

NOTE: INJECT ONE SIDE IN NORMAL & OTHER SIDE HARMONICS, INCREASE THE HS1 SETTING.

HV SIDE

| Phase | Setting | Expected | Pickup (A) | Timing (ms) |
| --- | --- | --- | --- | --- |
| R – E | 15 pu | 16.4 |  |  |
| Y – E | 15 pu | 16.4 |  |  |
| B – E | 15 pu | 16.4 |  |  |
| R-Y-B | 15 pu | 10.93 |  |  |

Deviation: +/-5% Manual P64x/EN TD/A32 – Technical data – Page no. 42

LV SIDE

| Phase | Setting | Expected | Pickup (A) | Timing (ms) |
| --- | --- | --- | --- | --- |
| R – E | 15 pu | 16.4 |  |  |
| Y – E | 15 pu | 16.4 |  |  |
| B – E | 15 pu | 16.4 |  |  |
| R-Y-B | 15 pu | 10.93 |  |  |

Deviation: +/-5% Manual P64x/EN TD/A32 – Technical data – Page no. 4

- SLOPE K1 CHECK:

Objective: To check slope m1.

Test method:

Simulate differential and restraining currents such that they lie in the region over and under the curve.

Restraining current:

Ir = {(Ia * Kam,a) + (Ib * Kam,b) / 2 }

Differential current Id = (Ia * Kam,a) - (Ib * Kam,b)

Inject balanced currents in HV and LV windings.

Gradually increase HV current & keep LV current constant till relay operation. Note down value.

Idiff=k1*Ibias

In our case,   i) K1 = 0.3, Is1= 0.27

Please note that “Id” and “Ir” are derived by the relay after amplitude and vector group matching. Hence, we have to multiply injected currents by amplitude matching factors for calculation of “Id” and “Ir” , then we  substitute this value of “Ir” into characteristic equation, To find Theoretical value of Id.then compare with measure value of Id .

Setting: Slope:  0.3 ; IS1= 0.27 ; IS2= 2.0

Slope Condition: Is1/2 <= Ibias <= Is2

| Ref | HV CURRENT(A) | LV CURRENT(A) | Diff current(A) |  | Bias Current(A) |  | Slope |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Relay display | calculated | Relay display | calculated |  |
| R |  |  |  |  |  |  |  |
| Y |  |  |  |  |  |  |  |
| B |  |  |  |  |  |  |  |

- SLOPE K2 CHECK:

Objective       : To check slope m2 and threshold Is2.

Test method:  Simulate differential and restraining currents such that they lie in this region over and under the curve

Gradually increase HV current & keep LV current constant till relay operation. Note down value.

Idiff = K2*Ibias + Is2(K1-K2)

In our case, i) K1 = 0.3, K2= 0.8, Is1 = 0.27, Is2 = 2.0

Please note that “Id” and “Ir” are derived by the relay after amplitude and vector group matching. Hence, we have to multiply injected currents by amplitude matching factors for calculation of “Id” and “Ir”, then we substitute this value of “Ir” into characteristic equation, To find Theoretical value of Id, then compare with measure value of Id.

| Ref | HV CURRENT(A) | LV CURRENT(A) | Diff current(A) |  | Bias Current(A) |  | Slope |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Relay display | calculated | Relay display | calculated |  |
| R |  |  |  |  |  |  |  |
| Y |  |  |  |  |  |  |  |
| B |  |  |  |  |  |  |  |

% Slope=(Id2-Id1)/ (Ir2-Ir1) X100

- Diff 2nd HARMONIC RESTRAIN TEST(Setting= 15%)

| Phase | HV Current(A) @ 60Hz | LV current (A) @120Hz | Expected (A) | Actual (A) | Relay condition |
| --- | --- | --- | --- | --- | --- |
| R |  |  |  |  |  |
| Y |  |  |  |  |  |
| B |  |  |  |  |  |

Deviation: +/-10% Manual P63x/EN tTD/A32 – Technical data – Page no. 42

- Diff 5th HARMONIC RESTRAIN TEST(Setting= 25%)

| Phase | HV Current(A) @ 60Hz | LV current (A) @300Hz | Expected (A) | Actual (A) | Relay condition |
| --- | --- | --- | --- | --- | --- |
| R |  |  |  |  |  |
| Y |  |  |  |  |  |
| B |  |  |  |  |  |

Deviation: +/-10% Manual P64x/EN M/Aq6 – Technical data – Page no. 42

- CROSS BLOCKING:

- All Phase Checked ok.

- RESTRICTED EARTH FAULT PROTECTION:

NOTE:

REF protection is also following the same characteristic equation as like the differential function if only when you set low impedance it is applicable. And here we are introduce the scaling factor

Scaling factor = Neutral CTR/ Line CTR

Minimum pick up current of REF is

I= Is1/Scaling factor.

- HV SIDE LOW SET ELEMENT CURRENT SENSITIVITY TEST (Is1):

Objective: To test threshold Is1:

Test method:

Inject balanced currents in all phases (one by one)

Gradually increase currents till relay operation. Note down the value.

Calculation: For example Is1 = 0.1

Side a Pick up = Is1 / scaling factor =   0.150/1.0=0.150 A

Side b Pick up = Is1 /scaling factor =   0.150/1.0=0.150 A

Pick up Current Ib = 0.150 A

PICKUP TEST

| Side | Set Is1 ( A ) | Calculated Pick up Current ( A ) | Measured Current ( A ) |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | R Phase | Y Phase | B Phase |
| A HV | 0.15 | 0.150 |  |  |  |
| HV NCT | 0.15 | 0.150 |  |  |  |

Deviation: +/-5% Manual P64x/EN TD/A32 – Technical data – Page no. 42

TIMING TEST

| Side | Set Is1 ( A ) | Measured Time ( ms ) |  |  |
| --- | --- | --- | --- | --- |
|  |  | R Phase | Y Phase | B Phase |
| HV | 0.15 |  |  |  |
| HV NCT | 0.15 |  |  |  |

Setting: K1 =0 ; IS1= 0.10

- REF IN HV SIDE SLPE K1 TEST:

| Ref | HV PH CURRENT(A) | NUET CURRENT(A) | Diff current(A) |  | Bias Current(A) |  | % Slope |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Relay display | calculated | Relay display | calculated |  |
| 1 | 0.10 |  |  |  |  |  | 0 |
| 2 | 0.13 |  |  |  |  |  |  |

% Slope= (Id2-Id1)/(Ir2-Ir1) X 100

- REF IN HV SIDE SLPE K2 TEST:

Setting: K2= 150% ; IS2=1.0

| Ref | HV PHASE CURRENT(A) | NEUTRAL CURRENT(A) | Diff current(A) |  | Bias Current(A) |  | Slope |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Relay display | calculated | Relay display | calculated |  |
| R | 1.0 |  |  |  |  |  |  |
|  | 1.30 |  |  |  |  |  |  |

% Slope=(Id2-Id1)/ (Ir2-Ir1) X100

- LV SIDE LOW SET ELEMENT CURRENT SENSITIVITY TEST (Is1):

PICKUP TEST

| Side | Set Is1 ( A ) | Calculated Pick up Current ( A ) | Measured Current ( A ) |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | R Phase | Y Phase | B Phase |
| A HV | 0.11 | 0.11 |  |  |  |
| HV NCT | 0.11 | 0.11 |  |  |  |

Deviation: +/-5% Manual P64x/EN TD/A32 – Technical data – Page no. 42

TIMING TEST

| Side | Set Is1 ( A ) | Measured Time ( ms ) |  |  |
| --- | --- | --- | --- | --- |
|  |  | R Phase | Y Phase | B Phase |
| HV | 0.11 |  |  |  |
| HV NCT | 0.11 |  |  |  |

- REF IN LV SIDE SLPE K1 TEST:( Setting: K1 =0 ; IS1= 0.1)

| Ref | LV PHASE CURRENT(A) | NEUTRAL CURRENT(A) | Diff current(A) |  | Bias Current(A) |  | Slope |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Relay display | calculated | Relay display | calculated |  |
| R |  |  |  |  |  |  |  |

% Slope=(Id2-Id1)/ (Ir2-Ir1) X100

- REF IN LV SIDE SLPE K2 TEST:(Setting: K2= 150% ; IS2=      )

| Ref | LV PHASE CURRENT(A) | NEUTRAL CURRENT(A) | Diff current(A) |  | Bias Current(A) |  | Slope |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Relay display | calculated | Relay display | calculated |  |
| R |  |  |  |  |  |  |  |

% Slope=(Id2-Id1)/ (Ir2-Ir1) X100

- PHASE TIME INVERSE OVER CURRENT PROTECTION TEST:

HV SIDE

| PHASE | SETTING (A) | PICK UP (A) | DROP OFF (A) |
| --- | --- | --- | --- |
| A | 1.0 |  |  |
| B |  |  |  |
| C |  |  |  |

Set K Value = 0.275 ;  CURVE= NI

| Curve | Set Current ( A ) | Injected Current ( A ) | Operating Time ( sec ) |  |  | Limit ( As Per Curve ) (sec) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | R Phase | Y Phase | B Phase |  |
| SI | 1.0 | 2.0 |  |  |  | 2.75+/-5% |

Deviation: +/-5%   Manual P64x/EN TD/A32 – Technical data – Page no. 42

LV SIDE

| PHASE | SETTING (A) | PICK UP (A) | DROP OFF (A) |
| --- | --- | --- | --- |
| A | 1.0 |  |  |
| B |  |  |  |
| C |  |  |  |

Set K Value = 0.25  ;  CURVE= NI

| Curve | Set Current ( A ) | Injected Current ( A ) | Operating Time ( sec ) |  |  | Limit ( As Per Curve ) (sec) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | R Phase | Y Phase | B Phase |  |
| SI | 1.0 | 2.0 |  |  |  | 2.50+/-5% |

Deviation: +/-5%   Manual P64x/EN TD/A32 – Technical data – Page no. 42

- EARTH FAULT TIME INVERSE PROTECTION TEST:

HV SIDE

| PHASE | SETTING (A) | PICK UP (A) | DROP OFF (A) |
| --- | --- | --- | --- |
| N | 0.22 |  |  |

Set K Value = 0.25

| Curve | Set Current ( A ) | Injected Current ( A ) | Operating Time ( sec ) | Limit ( As Per Curve ) (sec) |
| --- | --- | --- | --- | --- |
| SI | 0.22 | 0.44 |  | 2.5 +/-5% |

Deviation: +/-5%   Manual P64x/EN TD/A32 – Technical data – Page no. 42

LV SIDE

| PHASE | SETTING (A) | PICK UP (A) | DROP OFF (A) |
| --- | --- | --- | --- |
| N | 0.18 |  |  |

Set K Value = 0.25

| Curve | Set Current ( A ) | Injected Current ( A ) | Operating Time ( sec ) | Limit ( As Per Curve ) (sec) |
| --- | --- | --- | --- | --- |
| SI | 0.18 | 0.36 |  | 2.5 +/-5% |

Deviation: +/-5%   Manual P64x/EN TD/A32 – Technical data – Page no. 42

- STANDBY EARTH FAULT PROTECTION TEST:

Set TMS = 0.12 ; PRI= 120 A ; CTR=1000/1 A; SEC= 0.12

| CURVE | SET CURRENT | INJECTED CURRENT | MEASURED TIME (sec) | LIMIT (AS PER CURVE) (sec) |
| --- | --- | --- | --- | --- |
| LTI | 0.12 | 0.24 |  | 18.0 +/-5% |

- NEUTRAL CURRENT ALARM PROTECTION(51NA) :

Setting: PRI= 80 A, CTR=1000/1 A; SEC= 0.08 A

| SETTING | PICKUP (A) | DROPOFF (A) | Exp. TIME (s) | ACTUAL TIME (s) |
| --- | --- | --- | --- | --- |
| 0.08 |  |  |  |  |

- CB FAIL FUNCTION CHECK:

Simulate CBF initiation simultaneously with fault condition and check CBF trip and Timing.

| Fault Type | Check CBF Inti.On Relay | CBF-2 Set Time | Measured Time |
| --- | --- | --- | --- |
| External Initiation |  |  |  |

- UNDER FREQUENCY ELEMENT TEST:

PICK UP TEST:

| Stages | Set Frequency ( Hz ) | Applied Voltage ( V ) | Measured Frequency (Hz) |  |
| --- | --- | --- | --- | --- |
|  |  |  | Pick up | Drop off |
| F˂1 |  |  |  |  |
| F˂2 |  |  |  |  |
| F˂3 |  |  |  |  |
| F˂4 |  |  |  |  |

Deviation: +/-0.01Hz Manual P64x/EN TD/A32 – Technical data – Page no. 43

TIMING TEST:

| Stages | Set Frequency ( Hz ) | Applied Voltage ( V ) | Set time (sec) | Measured Time (sec) |
| --- | --- | --- | --- | --- |
| F˂1 |  |  |  |  |
| F˂2 |  |  |  |  |
| F˂3 |  |  |  |  |
| F˂4 |  |  |  |  |

Operating time: ˂70mS   Manual P64x/EN TD/A32 – Technical data – Page no. 43

- BINARY INPUT OPERATION CHECK:

| Input No. | Terminal No. |  | Active | Function Assigned | Remarks |
| --- | --- | --- | --- | --- | --- |
|  | ( + ) | ( - ) |  |  |  |
| OPTO 1 | D2 | D1 | High |  |  |
| OPTO 2 | D4 | D3 | High |  |  |
| OPTO 3 | D6 | D5 | High |  |  |
| OPTO 4 | D8 | D7 | High |  |  |
| OPTO 5 | D10 | D9 | High |  |  |
| OPTO 6 | D12 | D11 | High |  |  |
| OPTO 7 | D14 | D13 | High |  |  |
| OPTO 8 | D16 | D15 | High |  |  |
| OPTO 9 | F2 | F1 | High |  |  |
| OPTO 10 | F4 | F3 | High |  |  |
| OPTO 11 | F6 | F5 | High |  |  |
| OPTO 12 | F8 | F7 | High |  |  |
| OPTO 13 | F10 | F9 | High |  |  |
| OPTO 14 | F12 | F11 | High |  |  |
| OPTO 15 | F14 | F13 | High |  |  |
| OPTO 16 | F16 | F15 | High |  |  |
| OPTO 17 | B2 | B1 | High |  |  |
| OPTO 18 | B4 | B3 | High |  |  |
| OPTO 19 | B6 | B5 | High |  |  |
| OPTO 20 | B8 | B7 | High |  |  |
| OPTO 21 | B10 | B9 | High |  |  |
| OPTO 22 | B12 | B11 | High |  |  |
| OPTO 23 | B14 | B13 | High |  |  |
| OPTO 24 | B16 | B15 | High |  |  |

- BINARY OUTPUT CONTACT CHECK:

| Output No. | Terminal No. | Type | Function Assigned | OUTPUT Checked |
| --- | --- | --- | --- | --- |
| RL1 | H1-H2 | NO |  |  |
| RL2 | H3-H4 | NO |  |  |
| RL3 | H5-H6 | NO |  |  |
| RL4 | H7-H8 | NO |  |  |
| RL5 | H9-H10 | NO |  |  |
| RL6 | H11-H12 | NO |  |  |
| RL7 | H15-H13 | NC |  |  |
|  | H15-H14 | NO |  |  |
| RL8 | H18-H16 | NC |  |  |
|  | H18-H17 | NO |  |  |
| RL9 | G1-G2 | NO |  |  |
| RL10 | G3-G4 | NO |  |  |
| RL11 | G5-G6 | NO |  |  |
| RL12 | G7-G8 | NO |  |  |
| RL13 | G9-G10 | NO |  |  |
| RL14 | G11-G12 | NO |  |  |
| RL15 | G15-G13 | NC |  |  |
|  | G15-G14 | NO |  |  |
| RL16 | G18-G16 | NC |  |  |
|  | G18-G17 | NO |  |  |

- FIXED LED INDICATIONS TEST:

| LED No. | LED Label | Colour | Result |
| --- | --- | --- | --- |
| LED 1 | Trip | RED |  |
| LED 2 | Alarm | YELLOW |  |
| LED 3 | Out of Service | YELLOW |  |
| LED 4 | Healthy | GREEN |  |

- LED INDICATIONS TEST: (LEFT SIDE LED)

| LED No. | LED Label | Colour | Result |
| --- | --- | --- | --- |
| LED 1 | DIFF TRIP | RED |  |
| LED 2 | R PH OPTD | RED |  |
| LED 3 | Y PH OPTD | RED |  |
| LED 4 | B PH OPTD | RED |  |
| LED 5 | HV REF OPTD | RED |  |
| LED 6 | LV REF OPTD | RED |  |
| LED 7 | O/C OPTD | RED |  |
| LED 8 | E/F OPTD | RED |  |

- LED INDICATIONS TEST: (RIGHT SIDE FUNCTIONAL LED)

| LED No. | LED Label | Colour | Result |
| --- | --- | --- | --- |
| LED 1 | SBEF OPTD | RED |  |
| LED 2 | MECH PROT. OPTD | RED |  |
| LED 3 | CBF-2 OPTD | RED |  |
| LED 4 | CBF-2 INIT | YELLOW |  |
| LED 5 | SBEF ALARM | YELLOW |  |
| LED 6 | U/F STG-1 OPTD | RED |  |
| LED 7 | U/F STG-2 OPTD | RED |  |
| LED 8 | U/F STG-2 OPTD | RED |  |
| LED 9 | U/F STG-3 OPTD | RED |  |
| LED 10 | 2nd HARMONIC BLOCK | RED |  |
|  | 5th HARMONIC BLOCK | GREEN |  |