1.GENERAL DATA AND INFORMATION

| # Designation No | : 50/51-50N/51N | Rated Current | : For Phase : |
| --- | --- | --- | --- |
| Manufacturer | : ABB |  | : For Neutral : |
| Model No. | : REQ650 | # CT Ratio | : |
| Sl.No. | : | # VT Ratio | : |
| # Frequency | : 60.00 Hz | # Aux. Supply | : 100-240V AC ,48- 250V DC |

..\WorkInstructions\64.pdf

For Mechanical Check/Visual Inspection and Electrical Tests Use C.L. of W.I.64

2. SECONDARY INJECTION TEST

2.1. MEASUREMENT CHECKS

| Phase | Injected current (A) | Measured Current (A) | Remarks |
| --- | --- | --- | --- |
| RN |  |  |  |
| YN |  |  |  |
| BN |  |  |  |

2.2 FOUR STEP PHASE  OVERCURRENT PROTECTION: (OC4PTOC)

Limits :

STAGE 1

| PHASE | SETTING (A) | PICK UP (A) | DROP OFF (A) |
| --- | --- | --- | --- |
| A | 1.0 |  |  |
| B |  |  |  |
| C |  |  |  |

STAGE 2

| PHASE | SETTING (A) | PICK UP (A) | DROP OFF (A) |
| --- | --- | --- | --- |
| A | 2.0 |  |  |
| B |  |  |  |
| C |  |  |  |

STAGE 3

| PHASE | SETTING (A) | PICK UP (A) | DROP OFF (A) |
| --- | --- | --- | --- |
| A | 3.0 |  |  |
| B |  |  |  |
| C |  |  |  |

STAGE 4

| PHASE | SETTING (A) | PICK UP (A) | DROP OFF (A) |
| --- | --- | --- | --- |
| A | 4.0 |  |  |
| B |  |  |  |
| C |  |  |  |

OPERATING TIME STAGE (1&2)

TMS=1.0				Limit : ±0.05% of set time or ±10ms

| Curve | Cal. time @ 3* IS | Measured time (sec) |  |  | Limit |
| --- | --- | --- | --- | --- | --- |
|  |  | Phase | Stage 1 | Stage 2 |  |
| IEC standard inverse | 6.3 | C |  |  | 5.985 – 6.615 |
| IEC very inverse | 6.75 | A |  |  | 6.413 – 7.087 |
| IEC ext. inverse | 10 | B |  |  | 9.5 – 10.5 |
| IEC Long time inverse | 60 | A |  |  | 57.0 – 63.0 |
| IEC Definite time | 1.0 | B |  |  | 0.95 – 1.05 |

OPERATING TIME STAGE (3&4)

| Phase | Setting (Sec.) |  | Measured (Sec.) |  |
| --- | --- | --- | --- | --- |
|  | Stage 3 | Stage 4 | Stage 3 | Stage 4 |
| A | 0.5 | 0.1 |  |  |
| B |  |  |  |  |
| C |  |  |  |  |

2.3 FOUR STEP  RESIDUAL  OVERCURRENT PROTECTION: (EF4PTOC)

Limits :

STAGE 1

| PHASE | SETTING (A) | PICK UP (A) | DROP OFF (A) |
| --- | --- | --- | --- |
| N |  |  |  |

STAGE 2

| PHASE | SETTING (A) | PICK UP (A) | DROP OFF (A) |
| --- | --- | --- | --- |
| N |  |  |  |

STAGE 3

| PHASE | SETTING (A) | PICK UP (A) | DROP OFF (A) |
| --- | --- | --- | --- |
| N |  |  |  |

STAGE 4

| PHASE | SETTING (A) | PICK UP (A) | DROP OFF (A) |
| --- | --- | --- | --- |
| N |  |  |  |

OPERATING TIME STAGE (1&2)

TMS=1.0				Limit : ±0.05% of set time or ±10ms

| Curve | Cal. time @ 3* IS | Measured time (sec) |  |  | Limit |
| --- | --- | --- | --- | --- | --- |
|  |  | Phase | Stage 1 | Stage 2 |  |
| IEC standard inverse | 6.3 | C |  |  | 5.985 – 6.615 |
| IEC very inverse | 6.75 | A |  |  | 6.413 – 7.087 |
| IEC ext. inverse | 10 | B |  |  | 9.5 – 10.5 |
| IEC Long time inverse | 60 | A |  |  | 57.0 – 63.0 |
| IEC Definite time | 1.0 | B |  |  | 0.95 – 1.05 |

OPERATING TIME STAGE (3&4)

| Phase | Setting (Sec.) |  | Measured (Sec.) |  |
| --- | --- | --- | --- | --- |
|  | Stage 3 | Stage 4 | Stage 3 | Stage 4 |
| N | 0.5 | 0.1 |  |  |

2.4  BREAKER FAIL PROTECTION (CCRBRF):

| FUNCTION MODE | Pickup set value (A) | Measured Pickup (A) | Trip time (Sec) |  |  |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Set Value |  | Measured Value |  |  |
|  |  |  | T1 | T2 | T1 | T2 |  |
| Current and BuTrip Mode= 1out of 3 or 2 out of 4 | IP> = 0.2 |  |  |  |  |  |  |
| Current and BuTrip Mode= 1out of 3 or 2 out of 4 | IN> = 0.1 |  |  |  |  |  |  |

Limits:

- 5-Binary Input Check:-

| Sno: | Description | TERMINALS | Checked | Remarks |
| --- | --- | --- | --- | --- |
| - BI 1 |  | - X120 (1,2) |  |  |
| - BI 2 |  | - X120 (3,2) |  |  |
| - BI 3 |  | - X120 (4,2) |  |  |
| - BI 4 |  | - X120 (5,6) |  |  |
| - BI1 |  | X110 (1,2) |  |  |
| - BI 2 |  | X110 (3,4) |  |  |
| - BI3 |  | X110 (5,6) |  |  |
| - BI 4 |  | X110 (6,7) |  |  |
| - BI 5 |  | X110 (8,9) |  |  |
| - BI 6 |  | X110 (9,10) |  |  |
| - BI 7 |  | X110 (11,12) |  |  |
| - BI 8 |  | X110 (12,13) |  |  |
| - BI 1 |  | - X130 (1,2) |  |  |
| - BI 2 |  | X130 (3,4) |  |  |
| - BI 3 |  | X130 (5,6) |  |  |
| - BI 4 |  | X130 (7,8) |  |  |

- 6-  Binary Outputs Check:-

| Sno: | Description | TERMINALS | Checked | Remarks |
| --- | --- | --- | --- | --- |
| - P01 |  | - X100 (6,7) |  |  |
| - P02 |  | X100 (8,9) |  |  |
| - S01 |  | X100 (10,11,12) |  |  |
| - S02 |  | X100 (13,14) |  |  |
| - P03 |  | X100 (16,18) |  |  |
| - P04 |  | X100 (22,24) |  |  |
| - S01 |  | - X110 (14,15) |  |  |
| - S02 |  | - X110 (17,18) |  |  |
| - S03 |  | - X110 (20,21) |  |  |
| - S04 |  | - X110 (23,24) |  |  |