..\WorkInstructions\81.pdf

For Mechanical Check/Visual Inspection and Electrical Tests Use C.L. of W.I.81

- GENERAL  DATA AND INFORMATION :

| PANEL NO |  |
| --- | --- |
| PANEL NAME |  |
| TYPE |  |
| MANUFACTURER |  |
| SERIAL NO |  |

2.      MECHANICAL CHECKS AND VISUAL INSPECTION

3.  ELECTRICAL TESTS

| Input channels BIM:3 | Function Duty | Result |  |
| --- | --- | --- | --- |
| BI 01 | 13.8 KV CB (S120) CLOSE |  Yes |  N/A |
| BI 02 | 13.8 KV CB (S120) OPEN |  Yes |  N/A |
| BI 03 | 13.8 KV CB (S320) CLOSE |  Yes |  N/A |
| BI 04 | 13.8 KV CB (S320) OPEN |  Yes |  N/A |
| BI 05 | 13.8 KV BBP (SEC-AB) OPERATED |  Yes |  N/A |
| BI 06 | 13.8 KV BBP (SEC-BC) OPERATED |  Yes |  N/A |
| BI 07 | SPARE |  Yes |  N/A |
| BI 08 | ACSE IN TEST |  Yes |  N/A |
| BI 09 | GT-1 PROT OPTD |  Yes |  N/A |
| BI 10 | GT-2 PROT OPTD |  Yes |  N/A |
| BI 11 | GT-3 PROT OPTD |  Yes |  N/A |
| BI 12 | GT-1 (86BB/86CBF ) PROT OPTD |  Yes |  N/A |
| BI 13 | GT-2 (86BB/86CBF ) PROT OPTD |  Yes |  N/A |
| BI 14 | GT-3 (86BB/86CBF ) PROT OPTD |  Yes |  N/A |
| BI 15 | SPARE |  Yes |  N/A |
| BI 16 | SPARE |  Yes |  N/A |

| Input channels BIM: 5 | Function Duty | Result |  |
| --- | --- | --- | --- |
| BI 01 | GT-1 LV CB CLOSE |  Yes |  N/A |
| BI 02 | GT-1 LV CB OPEN |  Yes |  N/A |
| BI 03 | GT-2 LV CB CLOSE |  Yes |  N/A |
| BI 04 | GT-2 LV CB OPEN |  Yes |  N/A |
| BI 05 | GT-3 LV CB CLOSE |  Yes |  N/A |
| BI 06 | GT-3 LV CB OPEN |  Yes |  N/A |
| BI 07 | TOP IN |  Yes |  N/A |
| BI 08 | TOP OUT |  Yes |  N/A |
| BI 09 | GT-1 LV VT MCB ON |  Yes |  N/A |
| BI 10 | GT-1 LV VOLTAGE FAIL |  Yes |  N/A |
| BI 11 | GT-2 LV VT MCB ON |  Yes |  N/A |
| BI 12 | GT-2 LV VOLTAGE FAIL |  Yes |  N/A |
| BI 13 | GT-3 LV VT MCB ON |  Yes |  N/A |
| BI 14 | GT-3 LV VOLTAGE FAIL |  Yes |  N/A |
| BI 15 | SPARE |  Yes |  N/A |
| BI 16 | SPARE |  Yes |  N/A |

| Input channels BIM:6 | Function Duty | Result |  |
| --- | --- | --- | --- |
| BI 01 | GT-1 LV CB TOP REQUEST |  Yes |  N/A |
| BI 02 | GT-2 LV CB TOP REQUEST |  Yes |  N/A |
| BI 03 | GT-3 LV CB TOP REQUEST |  Yes |  N/A |
| BI 04 | BS-1 (S120) TOP REQUEST |  Yes |  N/A |
| BI 05 | BS-1 (S320) TOP REQUEST |  Yes |  N/A |
| BI 06 | TOP ABORT |  Yes |  N/A |
| BI 07 | ACSE ABORT |  Yes |  N/A |
| BI 08 | LED RESET |  Yes |  N/A |
| BI 09 | GT-1 (86BB/86CBF ) TRIP RELAY RESET |  Yes |  N/A |
| BI 10 | GT-2 (86BB/86CBF ) TRIP RELAY RESET |  Yes |  N/A |
| BI 11 | GT-3 (86BB/86CBF ) TRIP RELAY RESET |  Yes |  N/A |
| BI 12 | 13.8 KV BS1 PROTN RESET |  Yes |  N/A |
| BI 13 | 13.8 KV BS2 PROTN RESET |  Yes |  N/A |
| BI 14 | 5 CB IN SERVICE |  Yes |  N/A |
| BI 15 | ACSE IN |  Yes |  N/A |
| BI 16 | ACSE OUT |  Yes |  N/A |

| Input channels BOM :8 | Function Duty | Result |  |
| --- | --- | --- | --- |
| BO 01 | SPARE |  Yes |  N/A |
| BO 02 | SPARE |  Yes |  N/A |
| BO 03 | SPARE |  Yes |  N/A |
| BO 04 | SPARE |  Yes |  N/A |
| BO 05 | SPARE |  Yes |  N/A |
| BO 06 | SPARE |  Yes |  N/A |
| BO 07 | SPARE |  Yes |  N/A |
| BO 08 | SPARE |  Yes |  N/A |
| BO 09 | GT-1 LV CB OPEN CMD |  Yes |  N/A |
| BO 10 | SPARE |  Yes |  N/A |
| BO 11 | GT-1 LV CB CLOSE CMD |  Yes |  N/A |
| BO 12 | SPARE |  Yes |  N/A |
| BO 13 | GT-1 INTERLOCK |  Yes |  N/A |
| BO 14 | SPARE |  Yes |  N/A |
| BO 15 | GT-1 LV CB TOP SELECTED |  Yes |  N/A |
| BO 16 | SPARE |  Yes |  N/A |

| Input channels BOM :8 | Function Duty | Result |  |
| --- | --- | --- | --- |
| BO 17 | GT-2 LV CB OPEN CMD |  Yes |  N/A |
| BO 18 | SPARE |  Yes |  N/A |
| BO 19 | GT-2 LV CB CLOSE CMD |  Yes |  N/A |
| BO 20 | SPARE |  Yes |  N/A |
| BO 21 | GT-2 INTERLOCK |  Yes |  N/A |
| BO 22 | SPARE |  Yes |  N/A |
| BO 23 | GT-2 LV CB TOP SELECTED |  Yes |  N/A |
| BO 24 | SPARE |  Yes |  N/A |

| Input channels BOM :9 | Function Duty | Result |  |
| --- | --- | --- | --- |
| BO 01 | GT-3 LV CB OPEN CMD |  Yes |  N/A |
| BO 02 | SPARE |  Yes |  N/A |
| BO 03 | GT-3 LV CB CLOSE CMD |  Yes |  N/A |
| BO 04 | SPARE |  Yes |  N/A |
| BO 05 | GT-3 INTERLOCK |  Yes |  N/A |
| BO 06 | SPARE |  Yes |  N/A |
| BO 07 | GT-3 LV CB TOP SELECTED |  Yes |  N/A |
| BO 08 | SPARE |  Yes |  N/A |
| BO 09 | S120 LV CB OPEN CMD |  Yes |  N/A |
| BO 10 | SPARE |  Yes |  N/A |
| BO 11 | S120 LV CB CLOSE CMD |  Yes |  N/A |
| BO 12 | SPARE |  Yes |  N/A |
| BO 13 | S120 INTERLOCK |  Yes |  N/A |
| BO 14 | SPARE |  Yes |  N/A |
| BO 15 | S120 LV CB TOP SELECTED |  Yes |  N/A |
| BO 16 | SPARE |  Yes |  N/A |

| Input channels BOM :9 | Function Duty | Result |  |
| --- | --- | --- | --- |
| BO 17 | S320 LV CB OPEN CMD |  Yes |  N/A |
| BO 18 | SPARE |  Yes |  N/A |
| BO 19 | S320 LV CB CLOSE CMD |  Yes |  N/A |
| BO 20 | SPARE |  Yes |  N/A |
| BO 21 | S320 INTERLOCK |  Yes |  N/A |
| BO 22 | SPARE |  Yes |  N/A |
| BO 23 | S320 LV CB TOP SELECTED |  Yes |  N/A |
| BO 24 | SPARE |  Yes |  N/A |

ACSE SEQUENCE  TEST  :  1

STANDBY  BRK  :  GT 1

PROTECTION TRIP BRK : GT 2

| PROT OPTD | GT1 (OPEN) | GT2 (CLOSE) | GT3 (CLOSE) | S120 (CLOSE) | S320 (CLOSE) | FUNCTION EXPECTED |
| --- | --- | --- | --- | --- | --- | --- |
| 87T | CLOSE | OPEN | CLOSE | CLOSE | CLOSE |  |
| 86B | CLOSE | OPEN | CLOSE | CLOSE | CLOSE |  |
| 86CBF | CLOSE | OPEN | CLOSE | CLOSE | CLOSE |  |

FAILURE  OF SEQUENCE  :  ACSE FAIL  ALARM

ACSE SEQUENCE  TEST  :  2

STANDBY  BRK  :  GT 1

PROTECTION TRIP BRK : GT 3

| PROT OPTD | GT1 (OPEN) | GT2 (CLOSE) | GT3 (CLOSE) | S120 (CLOSE) | S320 (CLOSE) | FUNCTION EXPECTED |
| --- | --- | --- | --- | --- | --- | --- |
| 87T | CLOSE | CLOSE | OPEN | CLOSE | CLOSE |  |
| 86B | CLOSE | CLOSE | OPEN | CLOSE | CLOSE |  |
| 86CBF | CLOSE | CLOSE | OPEN | CLOSE | CLOSE |  |

FAILURE  OF SEQUENCE  :  ACSE FAIL  ALARM

ACSE SEQUENCE  TEST  :  3

STANDBY  BRK  :  GT 2

PROTECTION TRIP BRK : GT 1

| PROT OPTD | GT2 (OPEN) | GT3(CLOSE) | GT1 (CLOSE) | S120 (CLOSE) | S320 (CLOSE) | FUNCTION EXPECTED |
| --- | --- | --- | --- | --- | --- | --- |
| 87T | CLOSE | CLOSE | OPEN | CLOSE | CLOSE |  |
| 86B | CLOSE | CLOSE | OPEN | CLOSE | CLOSE |  |
| 86CBF | CLOSE | CLOSE | OPEN | CLOSE | CLOSE |  |

FAILURE  OF SEQUENCE  :  ACSE FAIL  ALARM

ACSE SEQUENCE  TEST  :  4

STANDBY  BRK  :  GT 2

PROTECTION TRIP BRK : GT 3

| PROT OPTD | GT2 (OPEN) | GT1 (CLOSE) | GT3 (CLOSE) | S120 (CLOSE) | S320 (CLOSE) | FUNCTION EXPECTED |
| --- | --- | --- | --- | --- | --- | --- |
| 87T | CLOSE | CLOSE | OPEN | CLOSE | CLOSE |  |
| 86B | CLOSE | CLOSE | OPEN | CLOSE | CLOSE |  |
| 86CBF | CLOSE | CLOSE | OPEN | CLOSE | CLOSE |  |

FAILURE  OF SEQUENCE  :  ACSE FAIL  ALARM

ACSE SEQUENCE  TEST  :  5

STANDBY  BRK  :  GT 3

PROTECTION TRIP BRK : GT 1

| PROT OPTD | GT3 (OPEN) | GT2 (CLOSE) | GT1 (CLOSE) | S120 (CLOSE) | S320 (CLOSE) | FUNCTION EXPECTED |
| --- | --- | --- | --- | --- | --- | --- |
| 87T | CLOSE | CLOSE | OPEN | CLOSE | CLOSE |  |
| 86B | CLOSE | CLOSE | OPEN | CLOSE | CLOSE |  |
| 86CBF | CLOSE | CLOSE | OPEN | CLOSE | CLOSE |  |

FAILURE  OF SEQUENCE  :  ACSE FAIL  ALARM

ACSE SEQUENCE  TEST  :  6

STANDBY  BRK  :  GT 3

PROTECTION TRIP BRK : GT 2

| PROT OPTD | GT3 (OPEN) | GT1 (CLOSE) | GT2 (CLOSE) | S120 (CLOSE) | S320 (CLOSE) | FUNCTION EXPECTED |
| --- | --- | --- | --- | --- | --- | --- |
| 87T | CLOSE | CLOSE | OPEN | CLOSE | CLOSE |  |
| 86B | CLOSE | CLOSE | OPEN | CLOSE | CLOSE |  |
| 86CBF | CLOSE | CLOSE | OPEN | CLOSE | CLOSE |  |

FAILURE  OF SEQUENCE  :  ACSE FAIL  ALARM

ACSE SEQUENCE  TEST  :  7

STANDBY  BRK  : S120

PROTECTION TRIP BRK : GT 1

| PROT OPTD | GT1 (CLOSE) | GT2 (CLOSE) | GT3 (CLOSE) | S120 (OPEN) | S320 (CLOSE) | FUNCTION EXPECTED |
| --- | --- | --- | --- | --- | --- | --- |
| 87T | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |
| 86B | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |
| 86CBF | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |

FAILURE  OF SEQUENCE  :  ACSE FAIL  ALARM

ACSE SEQUENCE  TEST  :  8

STANDBY  BRK  : S120

PROTECTION TRIP BRK : GT 2

| PROT OPTD | GT2 (CLOSE) | GT1 (CLOSE) | GT3 (CLOSE) | S120 (OPEN) | S320 (CLOSE) | FUNCTION EXPECTED |
| --- | --- | --- | --- | --- | --- | --- |
| 87T | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |
| 86B | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |
| 86CBF | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |

FAILURE  OF SEQUENCE  :  ACSE FAIL  ALARM

ACSE SEQUENCE  TEST  :  9

STANDBY  BRK  : S120

PROTECTION TRIP BRK : GT 3

| PROT OPTD | GT3 (CLOSE) | GT2 (CLOSE) | GT1 (CLOSE) | S120 (OPEN) | S320 (CLOSE) | FUNCTION EXPECTED |
| --- | --- | --- | --- | --- | --- | --- |
| 87T | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |
| 86B | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |
| 86CBF | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |

FAILURE  OF SEQUENCE  :  ACSE FAIL  ALARM

ACSE SEQUENCE  TEST  :  10

STANDBY  BRK  : S320

PROTECTION TRIP BRK : GT 1

| PROT OPTD | GT1 (CLOSE) | GT2 (CLOSE) | GT3 (CLOSE) | S320 (OPEN) | S120 (CLOSE) | FUNCTION EXPECTED |
| --- | --- | --- | --- | --- | --- | --- |
| 87T | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |
| 86B | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |
| 86CBF | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |

FAILURE  OF SEQUENCE  :  ACSE FAIL  ALARM

ACSE SEQUENCE  TEST  :  11

STANDBY  BRK  : S320

PROTECTION TRIP BRK : GT 2

| PROT OPTD | GT2 (CLOSE) | GT1 (CLOSE) | GT3 (CLOSE) | S320 (OPEN) | S120 (CLOSE) | FUNCTION EXPECTED |
| --- | --- | --- | --- | --- | --- | --- |
| 87T | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |
| 86B | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |
| 86CBF | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |

FAILURE  OF SEQUENCE  :  ACSE FAIL  ALARM

ACSE SEQUENCE  TEST  :  12

STANDBY  BRK  : S320

PROTECTION TRIP BRK : GT 3

| PROT OPTD | GT3 (CLOSE) | GT2 (CLOSE) | GT1 (CLOSE) | S320 (OPEN) | S120 (CLOSE) | FUNCTION EXPECTED |
| --- | --- | --- | --- | --- | --- | --- |
| 87T | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |
| 86B | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |
| 86CBF | OPEN | CLOSE | CLOSE | CLOSE | CLOSE |  |

FAILURE  OF SEQUENCE  :  ACSE FAIL  ALARM

ACSE  SEQUENCE TEST : 13

STANDBY  BRK : GT1

PROTECTION  OPTD :  STUCK

| PROTECTION OPERATED | BREAKER STATUS | BREAKER STATUS |  |  |  |  | REMARK | FUNCTION AS EXPTD |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | GT1 | GT2 | GT3 | S120 | S320 |  |  |
| STUCK A | BEFORE PROT.OPTD | OPEN | CLOSE | CLOSE | CLOSE | CLOSE | NO ACSE START |  |
|  | AFTER PROT.OPTD | OPEN | CLOSE | CLOSE | OPEN | CLOSE |  |  |
| STUCK B | BEFORE PROT.OPTD | OPEN | CLOSE | CLOSE | CLOSE | CLOSE | ACSE START/GT1 CLOSE |  |
|  | AFTER PROT.OPTD | CLOSE | OPEN | CLOSE | OPEN | OPEN |  |  |
| STUCK C | BEFORE PROT.OPTD | OPEN | CLOSE | CLOSE | CLOSE | CLOSE | ACSE START/GT1 CLOSE |  |
|  | AFTER PROT.OPTD | CLOSE | CLOSE | OPEN | CLOSE | OPEN |  |  |

ACSE  SEQUENCE TEST : 14

STANDBY  BRK : GT2

PROTECTION  OPTD :  STUCK

| PROTECTION OPERATED | BREAKER STATUS | BREAKER STATUS |  |  |  |  | REMARK | FUNCTION AS EXPTD |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | GT2 | GT1 | GT3 | S120 | S320 |  |  |
| STUCK A | BEFORE PROT.OPTD | OPEN | CLOSE | CLOSE | CLOSE | CLOSE | ACSE START/GT2 CLOSE |  |
|  | AFTER PROT.OPTD | CLOSE | OPEN | CLOSE | OPEN | CLOSE |  |  |
| STUCK B | BEFORE PROT.OPTD | OPEN | CLOSE | CLOSE | CLOSE | CLOSE | NO ACSE START |  |
|  | AFTER PROT.OPTD | OPEN | CLOSE | CLOSE | OPEN | OPEN |  |  |
| STUCK C | BEFORE PROT.OPTD | OPEN | CLOSE | CLOSE | CLOSE | CLOSE | ACSE START/GT2 CLOSE |  |
|  | AFTER PROT.OPTD | CLOSE | CLOSE | OPEN | CLOSE | OPEN |  |  |

ACSE  SEQUENCE TEST : 15

STANDBY  BRK : GT3

PROTECTION  OPTD :  STUCK

| PROTECTION OPERATED | BREAKER STATUS | BREAKER STATUS |  |  |  |  | REMARK | FUNCTION AS EXPTD |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | GT3 | GT2 | GT1 | S120 | S320 |  |  |
| STUCK A | BEFORE PROT.OPTD | OPEN | CLOSE | CLOSE | CLOSE | CLOSE | ACSE START/GT3 CLOSE |  |
|  | AFTER PROT.OPTD | CLOSE | CLOSE | OPEN | OPEN | CLOSE |  |  |
| STUCK B | BEFORE PROT.OPTD | OPEN | CLOSE | CLOSE | CLOSE | CLOSE | ACSE START/GT3 CLOSE |  |
|  | AFTER PROT.OPTD | CLOSE | OPEN | CLOSE | OPEN | OPEN |  |  |
| STUCK C | BEFORE PROT.OPTD | OPEN | CLOSE | CLOSE | CLOSE | CLOSE | NO ACSE START |  |
|  | AFTER PROT.OPTD | OPEN | CLOSE | CLOSE | CLOSE | OPEN |  |  |

ACSE  SEQUENCE TEST : 16

STANDBY  BRK : S120

PROTECTION  OPTD :  STUCK

| PROTECTION OPERATED | BREAKER STATUS | BREAKER STATUS |  |  |  |  | REMARK | FUNCTION AS EXPTD |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | GT1 | GT2 | GT3 | S120 | S320 |  |  |
| STUCK A | BEFORE PROT.OPTD | CLOSE | CLOSE | CLOSE | OPEN | CLOSE | NO ACSE START |  |
|  | AFTER PROT.OPTD | OPEN | CLOSE | CLOSE | OPEN | CLOSE |  |  |
| STUCK B | BEFORE PROT.OPTD | CLOSE | CLOSE | CLOSE | OPEN | CLOSE | NO ACSE START |  |
|  | AFTER PROT.OPTD | CLOSE | OPEN | CLOSE | OPEN | OPEN |  |  |
| STUCK C | BEFORE PROT.OPTD | CLOSE | CLOSE | CLOSE | OPEN | CLOSE | ACSE START/S120 CLOSE |  |
|  | AFTER PROT.OPTD | CLOSE | CLOSE | OPEN | CLOSE | OPEN |  |  |

ACSE  SEQUENCE TEST : 17

STANDBY  BRK : S320

PROTECTION  OPTD :  STUCK

| PROTECTION OPERATED | BREAKER STATUS | BREAKER STATUS |  |  |  |  | REMARK | FUNCTION AS EXPTD |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | GT1 | GT2 | GT3 | S120 | S320 |  |  |
| STUCK A | BEFORE PROT.OPTD | CLOSE | CLOSE | CLOSE | CLOSE | OPEN | ACSE START/S320 CLOSE |  |
|  | AFTER PROT.OPTD | OPEN | CLOSE | CLOSE | OPEN | CLOSE |  |  |
| STUCK B | BEFORE PROT.OPTD | CLOSE | CLOSE | CLOSE | CLOSE | OPEN | NO ACSE START |  |
|  | AFTER PROT.OPTD | CLOSE | OPEN | CLOSE | OPEN | OPEN |  |  |
| STUCK C | BEFORE PROT.OPTD | CLOSE | CLOSE | CLOSE | CLOSE | OPEN | NO ACSE START |  |
|  | AFTER PROT.OPTD | CLOSE | CLOSE | OPEN | CLOSE | OPEN |  |  |

TIMER  SETTINGS  FOR SEQUENCE  OPERATIONS  :

RESET  TIMER   :  3 Sec

AUTO  CHANGE OVER  SWITCHING  FAILED (INDICATION ) :  150 Sec (After starting sequence operation )

CLOSING  OPERATION   :  500 msec

TOP  FAILED   :    60  SEC

TOP SEQUENCE TEST  : 1

BREAKER UNDER TOP  :   GT1

| BREAKER CLOSED MANUALLY | GT1 STATUS | FUNCTION AS EXPECTED |
| --- | --- | --- |
| GT2 | TRIPPED |  |
| GT3 | TRIPPED |  |
| S120 | TRIPPED |  |
| S320 | TRIPPED |  |

TOP SEQUENCE TEST  : 2

BREAKER UNDER TOP  :   GT2

| BREAKER CLOSED MANUALLY | GT2 STATUS | FUNCTION AS EXPECTED |
| --- | --- | --- |
| GT1 | TRIPPED |  |
| GT3 | TRIPPED |  |
| S120 | TRIPPED |  |
| S320 | TRIPPED |  |

TOP SEQUENCE TEST  : 3

BREAKER UNDER TOP  :   GT3

| BREAKER CLOSED MANUALLY | GT3 STATUS | FUNCTION AS EXPECTED |
| --- | --- | --- |
| GT2 | TRIPPED |  |
| GT1 | TRIPPED |  |
| S120 | TRIPPED |  |
| S320 | TRIPPED |  |

TOP SEQUENCE TEST  : 4

BREAKER UNDER TOP  :   S120

| BREAKER CLOSED MANUALLY | S120 STATUS | FUNCTION AS EXPECTED |
| --- | --- | --- |
| GT2 | TRIPPED |  |
| GT3 | TRIPPED |  |
| GT1 | TRIPPED |  |
| S320 | TRIPPED |  |

TOP SEQUENCE TEST  : 5

BREAKER UNDER TOP  :   S320

| BREAKER CLOSED MANUALLY | S320` STATUS | FUNCTION AS EXPECTED |
| --- | --- | --- |
| GT2 | TRIPPED |  |
| GT3 | TRIPPED |  |
| GT1 | TRIPPED |  |
| S120 | TRIPPED |  |

ACSE  IN/OUT  COMMAND

| EQUIPMENT TO BE TESTED | FROM PANEL/FMK | INTIATION DEVICE/CONTACT | INDICATION AT RELAY PANEL | FMK INDICATION | FUNCTION AS EXPECTED |
| --- | --- | --- | --- | --- | --- |
| ACSE IN/OUT SELECTION | FROM PANEL IN/OUT FUNCTION | PRESS PB4 | PB4/H4 ACSE IN |  |  |
|  |  | PRESS PB5 | PB5/H5 ACSE OUT |  |  |

TOP  IN/OUT  COMMAND

| EQUIPMENT TO BE TESTED | FROM PANEL/FMK | INTIATION DEVICE/CONTACT | INDICATION AT RELAY PANEL | FMK INDICATION | FUNCTION AS EXPECTED |
| --- | --- | --- | --- | --- | --- |
| TOP IN/OUT SELECTION | FROM PANEL IN/OUT FUNCTION | PRESS TOP IN | TOP IN |  |  |
|  |  | PRESS TOP OUT | TOP OUT |  |  |

ALARMS  FROM  ACSE PANEL :

| ALARMS INTIATED SOURCE | ALARMS AT COMMON PANEL |
| --- | --- |
| MCB SWITCH OFF | ACSE SUPPLY FAIL /TRIP ON PARALLEL SYS FAULTY |
| 27C (15,16)(Supply fail), K12 (21,22) (watchdog alarm) | ACSE Faulty |
| K11 (31,32 - auto switching failed ) | AUTO C/O SWITCHING FAILED |
| SLR (9,10) | ACSE Remote off |