### A.GENERAL INFORMATION:

| Bay No. |  | Bay Name |  |
| --- | --- | --- | --- |
| Relay designation |  | Model No. |  |
| Make | ABB | S. No. |  |
| Rated Current | 1A | Rated Voltage |  |
| Frequency | 50/60 HZ | Aux. Voltage |  |

..\WorkInstructions\64.pdf

For Mechanical Check/Visual Inspection and Electrical Tests Use C.L. of W.I.64

### B. GENERAL CHECKS:

| Sl.no | General checks | Status |
| --- | --- | --- |
| 1. | Inspect for no physical damage. |  |
| 2. | Verify the wiring connection as per approved drawing. |  |
| 3. | Relay case connected to a local earth bar. |  |
| 4. | Power up the relay circuit and check relay is healthy. |  |
| 5. | Set the relay internal clock. |  |
| 6. | Send the relay setting configuration file to relay through Port F. |  |

C. MEASURMENTS CHECK:

CT Ratio:       600 /1 A

CURRENT INPUTS CHECK:

| Phase | Current (A) | Secondary Current on relay display (A) |  |  | Primary Current on relay display (A) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | R | Y | B | R | Y | B |
| L1-E | 1.0 |  |  |  |  |  |  |
| L2-E | 1.0 |  |  |  |  |  |  |
| L3-E | 1.0 |  |  |  |  |  |  |
| L1-L2-L3 | 1.0 |  |  |  |  |  |  |

VT Ratio: 13.8kV/115V

| Phase | Voltage (V) | Secondry Voltage on relay display in V |  |  | Primary Voltage on relay display in Kv |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | VRN | VYN | VBN | VRN | VYN | VBN |
| L1-E |  |  |  |  |  |  |  |
| L2-E |  |  |  |  |  |  |  |
| L3-E |  |  |  |  |  |  |  |
| L1-L2-L3 |  |  |  |  |  |  |  |

- SECONDARY INJECTION

  - Over Current Protection P/U & D/O Test:

    - Phase Over Current Protection Step 1:

| Phase | Set Current (A) | Pickup (A) | Drop off(A) | Remarks |
| --- | --- | --- | --- | --- |
| A | 0.660 |  |  |  |
| B | 0.660 |  |  |  |
| C | 0.660 |  |  |  |

    - Phase Over Current Protection Step 1 Operating Time :

| Phase | Set Time (ms) | Measured Time (ms) | Remarks |
| --- | --- | --- | --- |
| A | 500 |  |  |
| B | 500 |  |  |
| C | 500 |  |  |

    - Phase Over Current Protection Step 2:

| Phase | Set Current | Pickup | Drop off | Remarks |
| --- | --- | --- | --- | --- |
| A | 1.50 |  |  |  |
| B | 1.50 |  |  |  |
| C | 1.50 |  |  |  |

    - Phase Over Current Protection Step 2 Operating Time :

| Phase | Set Time (ms) | Measured Time (ms) | Remarks |
| --- | --- | --- | --- |
| A |  |  |  |
| B |  |  |  |
| C |  |  |  |

  - Earth fault Protection P/U & D/O Test:

    - Earth Fault Protection Step 1:

| Phase | Set Current (A) | Pickup (A) | Drop off (A) | Remarks |
| --- | --- | --- | --- | --- |
| N | 0.100 |  |  |  |

    - Earth Fault Protection Step 1 Operating Time :

| Phase | Set Time (ms) | Measured Time (ms) | Remarks |
| --- | --- | --- | --- |
| N | 500 |  |  |

    - Earth Fault Protection Step 2:

| Phase | Set Current | Pickup | Drop off | Remarks |
| --- | --- | --- | --- | --- |
| N | 1.50 |  |  |  |

    - Phase Over Current Protection Step 2 Operating Time :

| Phase | Set Time (ms) | Measured Time (ms) | Remarks |
| --- | --- | --- | --- |
| N | 100 |  |  |

  - Over Voltage Protection P/U & D/O Test:

    - Over Voltage Protection Step 1 (ALARM) :

| Phase | Set Voltage 105% | Pickup (V) | Drop off (V) | Remarks |
| --- | --- | --- | --- | --- |
| A |  |  |  |  |
| B |  |  |  |  |
| C |  |  |  |  |

    - Over Voltage Protection Step 1 Operating Time :

| Phase | Set Time (s) | Measured Time (s) | Remarks |
| --- | --- | --- | --- |
| A | 5.0 |  |  |
| B | 5.0 |  |  |
| C | 5.0 |  |  |

    - Over Voltage Protection Step 2 (TRIP):

| Phase | Set Voltage 110% | Pickup (V) | Drop off (V) | Remarks |
| --- | --- | --- | --- | --- |
| A |  |  |  |  |
| B |  |  |  |  |
| C |  |  |  |  |

    - Over Voltage Protection Step 2 Operating Time :

| Phase | Set Time (s) | Measured Time (s) | Remarks |
| --- | --- | --- | --- |
| A | 4.0 |  |  |
| B | 4.0 |  |  |
| C | 4.0 |  |  |

  - Under Voltage Protection P/U & D/O Test:

    - Under Voltage Protection Step 1 (ALARM) :

| Phase | Set Voltage 85% | Pickup (V) | Drop off (V) | Remarks |
| --- | --- | --- | --- | --- |
| A |  |  |  |  |
| B |  |  |  |  |
| C |  |  |  |  |

    - Under Voltage Protection Step 1 Operating Time :

| Phase | Set Time (s) | Measured Time (s) | Remarks |
| --- | --- | --- | --- |
| A | 5.0 |  |  |
| B | 5.0 |  |  |
| C | 5.0 |  |  |

    - Under Voltage Protection Step 2 (TRIP):

| Phase | Set Voltage 30% | Pickup (V) | Drop off (V) | Remarks |
| --- | --- | --- | --- | --- |
| A |  |  |  |  |
| B |  |  |  |  |
| C |  |  |  |  |

    - Under Voltage Protection Step 2 Operating Time :

| Phase | Set Time (s) | Measured Time (s) | Remarks |
| --- | --- | --- | --- |
| A |  |  |  |
| B |  |  |  |
| C |  |  |  |

  - Residual Over Voltage Protection P/U & D/O Test:

    - Residual Over Volatge Protection Step 1 (ALARM) :

| Phase | Set Value (30%) | Pickup Value | Drop off Value | Remarks |
| --- | --- | --- | --- | --- |
| N |  |  |  |  |

    - Residual Over Volatge Protection Step 1 Operating Time :

| Phase | Set Time (s) | Measured Time (s) | Remarks |
| --- | --- | --- | --- |
| N | 5.0 |  |  |

    - Residual Over Volatge Protection Step 1 (ALARM) :

| Phase | Set Value (40%) | Pickup Value | Drop off Value | Remarks |
| --- | --- | --- | --- | --- |
| N |  |  |  |  |

    - Residual Over Volatge Protection Step 1 Operating Time :

| Phase | Set Time (ms) | Measured Time (ms) | Remarks |
| --- | --- | --- | --- |
| N | 100 |  |  |

- Binary Output Check                                   (          )

| Card No. | O/P No. | Terminal No. | Function | REMARKS |
| --- | --- | --- | --- | --- |
| BOM4 | BO1 | X41:1 & 2 |  |  |
|  | BO2 | X41:3 & 2 |  |  |
|  | BO 3 | X41:4 & 5 |  |  |
|  | BO 4 | X41:6 & 5 |  |  |
|  | BO 5 | X41:7 & 8 |  |  |
|  | BO 6 | X41:9 & 8 |  |  |
|  | BO 7 | X41:10 & 11 |  |  |
|  | BO 8 | X41:12 & 11 |  |  |
|  | BO 9 | X41:13 & 14 |  |  |
|  | BO 10 | X41:15 & 14 |  |  |
|  | BO 11 | X41:16 & 17 |  |  |
|  | BO 12 | X41:18 & 17 |  |  |
|  | BO 13 | X42:1 & 2 |  |  |
|  | BO 14 | X42:3 & 2 |  |  |
|  | BO 15 | X42:4 & 5 |  |  |
|  | BO 16 | X42:6 & 5 |  |  |
|  | BO 17 | X42:7 & 8 |  |  |
|  | BO 18 | X42:9 & 8 |  |  |
|  | BO 19 | X42:10 & 11 |  |  |
|  | BO 20 | X42:12 & 11 |  |  |
|  | BO 21 | X42:13 & 14 |  |  |
|  | BO 22 | X42:15 & 14 |  |  |
|  | BO 23 | X42:16 & 17 |  |  |
|  | BO 24 | X42:18 & 17 |  |  |

- Binary Input Check                                 (        )

| Card No. | O/P No. | Terminal No. | Function | REMARKS |
| --- | --- | --- | --- | --- |
| BIM3 | BI 1 | X31:1 & 2 |  |  |
|  | BI 2 | X31:3 & 4 |  |  |
|  | BI 3 | X31:5 & 6 |  |  |
|  | BI 4 | X31:7 & 8 |  |  |
|  | BI 5 | X31:9 & 10 |  |  |
|  | BI 6 | X31:11 & 12 |  |  |
|  | BI 7 | X31:13 & 14 |  |  |
|  | BI 8 | X31:15 & 16 |  |  |
|  | BI 9 | X32:1 & 2 |  |  |
|  | BI 10 | X32:3 & 4 |  |  |
|  | BI 11 | X32:5 & 6 |  |  |
|  | BI 12 | X32:7 & 8 |  |  |
|  | BI 13 | X32:9 & 10 |  |  |
|  | BI 14 | X32:11 & 12 |  |  |
|  | BI 15 | X32:13 & 14 |  |  |
|  | BI 16 | X32:15 & 16 |  |  |

- LED Check                                                 (        )

| LED NO | LED COLOUR | FUNCTION | STATUS |
| --- | --- | --- | --- |
| 1 | RED |  |  |
| 2 | RED |  |  |
| 3 | RED |  |  |
| 4 | RED |  |  |
| 5 | RED |  |  |
| 6 | RED |  |  |
| 7 | YELLOW |  |  |
| 8 | YELLOW |  |  |
| 9 | YELLOW |  |  |
| 10 | YELLOW |  |  |
| 11 | YELLOW |  |  |
| 12 | YELLOW |  |  |
| 13 | YELLOW |  |  |
| 14 | YELLOW |  |  |
| 15 | YELLOW |  |  |

Test Equipment’s used:

| Sl. No | Description | Make | Equipment Sl .No | Calibration Date | Calibration Due Date |
| --- | --- | --- | --- | --- | --- |
| 1. |  |  |  |  |  |
| 2. |  |  |  |  |  |