### ..\WorkInstructions\64.pdf

For Mechanical Check/Visual Inspection and Electrical Tests Use C.L. of W.I.64

### A.GENERAL INFORMATION:

| Bay No. |  | Bay Name |  |
| --- | --- | --- | --- |
| Relay designation |  | Model No. | SEL-487V-R105-V0-Z002002-D20130320 |
| Make | SEL | S. No. |  |
| Rated Current | 1A | Rated Voltage |  |
| Frequency | 50/60 HZ | Aux. Voltage |  |

### B. GENERAL CHECKS:

| Sl.no | General checks | Status |
| --- | --- | --- |
| 1. | Inspect for no physical damage. |  |
| 2. | Verify the wiring connection as per approved drawing. |  |
| 3. | Relay case connected to a local earth bar. |  |
| 4. | Power up the relay circuit and check relay is healthy. |  |
| 5. | Set the relay internal clock. |  |
| 6. | Send the relay setting configuration file to relay through Port F. |  |

### C.  Control Input CHECK:

This is to verify the healthiness of the DC control inputs.

Apply a rated voltage at each input and verify the status of the input at Front panel or 5030 HMI.

Note:

- Open 5030 HMI view after the relay is connected to PC.

- Open “Device Overview” page name is  target  raw 31 to 34   and observe the Inputs status.

| Control input No. | Terminal | Configuration | Result |
| --- | --- | --- | --- |
| IN01 | A20-A21 |  |  |
| IN02 | A22-A23 |  |  |
| IN03 | A24-A25 |  |  |
| IN04 | A26-A27 |  |  |
| IN05 | A28-A29 |  |  |
| IN06 | A30-A31 |  |  |
| IN07 | A32-A31 |  |  |
| IN01 | B33-B34 |  |  |
| IN02 | B35-B36 |  |  |
| IN03 | B37-B38 |  |  |
| IN04 | B39-B40 |  |  |
| IN05 | B41-B42 |  |  |
| IN06 | B43-B44 |  |  |
| IN07 | B45-B46 |  |  |
| IN08 | B47-B48 |  |  |

### D. OUTPUT RELAY CHECK:

This is to verify the healthiness of the Control output relay healthiness.

Operate each output through front panel or 5030 HMI, the check continuity of the contact that closes.

Note: For PULSE the relay outputs, “Breaker” jumper shall be put ON position. This jumper is available in main board, which is on the top. Open the relay front cover, and change the jumper to ON position on main board.

- Open 5030 HMI view after the relay is connected to PC.

- Open “Control Window” page and Select the OUTPUT that you want to PULSE and select the duration of the PULSE.

- Execute the PULSE command. Verify the physical contact close of the corresponding output.

| Output Relay No. | Terminal | Configuration | Result |
| --- | --- | --- | --- |
| OUT01 | A01-A02 |  |  |
| OUT02 | A03-A04 |  |  |
| OUT03 | A05-A06 |  |  |
| OUT04 | A07-A08 |  |  |
| OUT05 | A09-A10 |  |  |
| OUT06 | A12-A11-A13 |  |  |
| OUT07 | A18-A17-A19 |  |  |
| OUT01 | B01-B02 |  |  |
| OUT02 | B03-B04 |  |  |
| OUT03 | B05-B06 |  |  |
| OUT04 | B07-B08 |  |  |
| OUT05 | B09-B10 |  |  |
| OUT06 | B11-B12 |  |  |
| OUT07 | B13-B14 |  |  |
| OUT08 | B15-B16 |  |  |
| OUT09 | B17-B18 |  |  |
| OUT10 | B19-B20 |  |  |
| OUT11 | B21-B22 |  |  |
| OUT12 | B23-B24 |  |  |
| OUT13 | B25-B26 |  |  |
| OUT14 | B27-B28- B29 |  |  |
| OUT15 | B30-B31- B32 |  |  |

E. MEASURMENTS CHECK:

Test Procedure

A. Current Measurement

Make connections as shown in test set up. Inject the current as per the table below and observe the reading on the relay display in primary and secondary values.

B. Voltage Measurement

Inject the Voltage as per the table below and observe the reading on the relay display in primary and secondary values.

CT Ratio:  600/1 A

VT Ratio: 13.8kV/100V

RMS METERING TERMINAL W

* The measurement current accuracy of the relay is ± 1 %.

- SECONDARY INJECTION

  - Over Current Protection P/U & D/O Test:

    - Phase Over Current Protection Step 1:

| Phase | Set Current (A) | Pickup (A) | Drop off(A) | Remarks |
| --- | --- | --- | --- | --- |
| A | 0.650 |  |  |  |
| B | 0.650 |  |  |  |
| C | 0.650 |  |  |  |

    - Phase Over Current Protection Step 1 Operating Time :

| Phase | Set Time (ms) | Measured Time (ms) | Remarks |
| --- | --- | --- | --- |
| A | 500 |  |  |
| B | 500 |  |  |
| C | 500 |  |  |

    - Phase Over Current Protection Step 2:

| Phase | Set Current | Pickup | Drop off | Remarks |
| --- | --- | --- | --- | --- |
| A | 1.50 |  |  |  |
| B | 1.50 |  |  |  |
| C | 1.50 |  |  |  |

    - Phase Over Current Protection Step 2 Operating Time :

| Phase | Set Time (ms) | Measured Time (ms) | Remarks |
| --- | --- | --- | --- |
| A | 100 |  |  |
| B | 100 |  |  |
| C | 100 |  |  |

  - Earth fault Protection P/U & D/O Test:

    - Earth Fault Protection Step 1:

| Phase | Set Current (A) | Pickup (A) | Drop off (A) | Remarks |
| --- | --- | --- | --- | --- |
| N | 0.100 |  |  |  |

    - Earth Fault Protection Step 1 Operating Time :

| Phase | Set Time (ms) | Measured Time (ms) | Remarks |
| --- | --- | --- | --- |
| N | 500 |  |  |

    - Earth Fault Protection Step 2:

| Phase | Set Current | Pickup | Drop off | Remarks |
| --- | --- | --- | --- | --- |
| N | 1.75 |  |  |  |

    - Phase Over Current Protection Step 2 Operating Time :

| Phase | Set Time (ms) | Measured Time (ms) | Remarks |
| --- | --- | --- | --- |
| N | 100 |  |  |

  - Over Voltage Protection P/U & D/O Test:

    - Over Voltage Protection Step 1 (ALARM) :

| Phase | Set Voltage 105% | Pickup (V) | Drop off (V) | Remarks |
| --- | --- | --- | --- | --- |
| ABC |  |  |  |  |

    - Over Voltage Protection Step 1 Operating Time :

| Phase | Set Time (s) | Measured Time (s) | Remarks |
| --- | --- | --- | --- |
| ABC | 5.0 |  |  |

    - Over Voltage Protection Step 2 (TRIP):

| Phase | Set Voltage 110% | Pickup (V) | Drop off (V) | Remarks |
| --- | --- | --- | --- | --- |
| ABC |  |  |  |  |

    - Over Voltage Protection Step 2 Operating Time :

| Phase | Set Time (s) | Measured Time (s) | Remarks |
| --- | --- | --- | --- |
| ABC | 4.0 |  |  |

  - Under Voltage Protection P/U & D/O Test:

    - Under Voltage Protection Step 1 (ALARM) :

| Phase | Set Voltage 85% | Pickup (V) | Drop off (V) | Remarks |
| --- | --- | --- | --- | --- |
| A |  |  |  |  |
| B |  |  |  |  |
| C |  |  |  |  |

    - Under Voltage Protection Step 1 Operating Time :

| Phase | Set Time (s) | Measured Time (s) | Remarks |
| --- | --- | --- | --- |
| A | 5.0 |  |  |
| B | 5.0 |  |  |
| C | 5.0 |  |  |

    - Under Voltage Protection Step 2 (TRIP):

| Phase | Set Voltage 30% | Pickup (V) | Drop off (V) | Remarks |
| --- | --- | --- | --- | --- |
| A |  |  |  |  |
| B |  |  |  |  |
| C |  |  |  |  |

    - Under Voltage Protection Step 2 Operating Time :

| Phase | Set Time (s) | Measured Time (s) | Remarks |
| --- | --- | --- | --- |
| A | 5.0 |  |  |
| B | 5.0 |  |  |
| C | 5.0 |  |  |

  - Residual Over Current Protection P/U & D/O Test:

    - Residual Over Current Protection Step 1:

| Phase | Set Value (A) | Pickup (A) | Drop off (A) | Remarks |
| --- | --- | --- | --- | --- |
| N |  |  |  |  |

    - Residual Over Volatge Protection Step 1 Operating Time :

| Phase | Set Time (s) | Measured Time (s) | Remarks |
| --- | --- | --- | --- |
| N | 5.0 |  |  |

    - Residual Over Volatge Protection Step 1 (ALARM) :

| Phase | Set Value (A) | Pickup (A) | Drop off (A) | Remarks |
| --- | --- | --- | --- | --- |
| N |  |  |  |  |

    - Residual Over Volatge Protection Step 1 Operating Time :

| Phase | Set Time (s) | Measured Time (s) | Remarks |
| --- | --- | --- | --- |
| N | 1.00 |  |  |

Test Equipment’s used:

| Sl. No | Description | Make | Equipment Sl .No | Calibration Date | Calibration Due Date |
| --- | --- | --- | --- | --- | --- |
| 1. |  |  |  |  |  |
| 2. |  |  |  |  |  |